## Slide 1
WIND TURBINE CONDITION MONITORING
Saving Millions in the Wind
How Physics, Machine Learning & Explainable AI Spot Failures Weeks in Advance
A Simplified Case Study: Foundations, Realized Approaches & Alternative Paths

## Slide 2
OPERATIONAL REALITY
The High Stakes of Wind Turbine Breakdowns
Why traditional reactive maintenance fails catastrophically at sea
The Machine
• Turbines are 300-ft tall robotic power plants with 80-meter blades.
• Internal components operate under titanic mechanical torque & cyclic stress.
• A 20-ton gearbox steps up rotor speed from 15 RPM to 1,500 RPM for the generator.
The Catastrophe
• Offshore crane ships cost $30,000+ per day just to mobilize.
• Replacing shattered gearboxes costs $150,000 to $250,000+ in parts.
• Rough winter seas can delay repairs for 6 to 8 weeks, losing hundreds of thousands in green power.
The Goal
• Spot component degradation 2 to 4 weeks before catastrophic failure.
• Use existing SCADA temperature and speed sensors without new hardware.
• Avoid false alarm fatigue so technicians genuinely trust the alerts.

## Slide 3
DATASET ANATOMY
Understanding the Benchmark (CARE_To_Compare)
89 years of real-world operational SCADA telemetry across 36 wind turbines
The Multi-Farm Architecture
Wind Farm A (Portugal, Onshore):
5 turbines, 22 datasets, 86 sensor channels. Transparent component breakdown from EDP Open Data.
Wind Farm B (Germany, Offshore):
15 datasets, 257 sensor channels. Severe marine environment, rotor bearing & transformer cell issues.
Wind Farm C (Germany, Offshore):
58 datasets, 957 sensor channels. Deep telemetry (pitch motors, converter IGBTs, blade heaters).
10-Minute Averaging (IEC 61400-25):
Raw milliseconds are aggregated into 10-minute average, min, max, and std deviation.
Structure of Each Monitored Event
Historical Baseline (train):
Exactly 1 full year (~52,000 observations) of normal healthy historical operation for that specific turbine.
Evaluation Window (prediction):
The subsequent 2 to 4 weeks. In anomaly datasets, degradation worsens leading to failure; in normal datasets, turbine keeps running.
Component Failure Modes:
Ground-truth failure logs catalog Gearbox breakdowns, Generator bearing wear, Transformer surges, and Hydraulic valve failures.
Balanced Benchmark:
44 labeled anomaly failure cases vs. 51 healthy normal control cases across the full repository.

## Slide 4
THEORETICAL CHALLENGE 1
The 'Status Code' Trap (Data Leakage)
Why a naive machine learning model achieves 99.9% accuracy but fails in operations
The Naive Shortcut (The Cheat)
• In raw SCADA files, 'status_type_id' records turbine states: 0 = Normal, 3 = Service, 4 = Downtime.
• When an anomaly dataset reaches breakdown, the status flips to 4 (Turbine is halted).
• A standard AI automatically latches onto status_type_id == 4 and claims 99.9% accuracy.
• WHY THIS IS USELESS: The wind farm already knows the turbine is down when it trips! Predicting downtime after the machine stops spinning has zero business value.
How We Resolved It (True Physics)
• We strictly erased status_type_id from all predictive features.
• The model must learn failure signatures exclusively from thermodynamic temperatures, vibrations, and aerodynamics.
• The entire prediction period is evaluated to detect early degradation while status is STILL 0 (Normal operation).
• OPERATIONAL OUTCOME: The model provides genuine early warning days before the emergency control system ever trips.

## Slide 5
THEORETICAL CHALLENGE 2
The Weather Trap & The 'Rising Fever' Fix
Is the bearing overheating, or is it just a sunny afternoon in July?
The Weather Confounding Problem
• A healthy gearbox bearing naturally runs at 60°C on a hot 38°C summer afternoon.
• A dying gearbox bearing might only reach 45°C on a freezing 2°C winter morning.
• If you feed raw temperatures to an AI, it classifies summer as an anomaly and misses winter failures!
• THE SCIENTIFIC CHALLENGE: How do we isolate genuine internal mechanical friction from external weather?
The Thermodynamic Solution (ΔT)
• Just like a doctor checks fever above normal room temperature, we engineered Differential Temperatures:
• ΔT = Component Temperature − Outside Ambient Temperature
• Subtracting ambient weather eliminates summer/winter bias and directly exposes bearing friction.
• Added Causal 6-Hour Moving Averages (RollMean 6h) to track sustained heat accumulation without future data leakage.

## Slide 6
THEORETICAL CHALLENGE 3
Generalizing to Unseen Strangers (Turbines)
Why random train/test splits lie, and how Leave-One-Turbine-Out validation proves reality
The Flaw of Random Splitting
• Turbines are like human beings: each has slight individual baselines.
• Turbine #11 might naturally run 1.5°C warmer than Turbine #0 due to its position on a ridge.
• If you randomly shuffle 10-minute records, the AI simply memorizes individual turbine IDs rather than universal physics.
• When deployed on a newly installed turbine, such models fail completely.
Leave-One-Turbine-Out Validation
• We erased turbine ID (asset_id) from all model input features.
• Enforced Leave-One-Turbine-Out Group Cross-Validation: Train on Turbines 0, 10, 11, 13 and evaluate on held-out Turbine 21.
• The model is forced to learn universal physical wear signatures that apply to ANY turbine.
• PROVEN RESULT: Achieved 0.83 Test AUC on completely unseen turbines in held-out validation.

## Slide 7
SOLUTION ARCHITECTURE
How We Built the Production System
A streamlined, high-speed pipeline combining physics, ensembles, and explainability
1. Data Hygiene
• Parsed semicolon delimiters.
• Audited 102M data points.
• Sparse NAs (<0.00004%) forward-filled with locf.
• Zero artificial values (no SMOTE).
2. Physics Features
• Delta T differentials for Gearbox, Generator, Transformer.
• Causal 6h rolling averages.
• Gear ratio (Gen RPM / Rotor RPM).
• Cp power conversion proxy.
3. High-Speed Models
• Benchmarked GLM, Random Forest, and XGBoost.
• Sub-second training (<1 sec).
• Compact memory footprint (109 MB RAM).
• Group CV across turbines.
4. Explainability & UI
• Exact TreeSHAP attributions.
• LIME local decision rules.
• Physical consistency verification.
• Production Shiny dashboard.

## Slide 8
ALTERNATIVE APPROACHES
What Other Approaches Could We Consider?
Evaluating deep learning, autoencoders, vibration FFTs, and synthetic sampling
Approach A: Deep Time-Series (LSTM / GRU / Transformers)
Recurrent or attention networks modeling long sequential dependencies directly from raw time-steps.
Approach B: Unsupervised Autoencoders (Normal Behavior Modeling)
Neural networks trained only on healthy data to predict expected values; high reconstruction error signals fault.
Approach C: Classical Vibration Signal Processing (FFT / Envelope)
Fourier transforms and spectral analysis on high-frequency (kHz) accelerometers placed on bearing housings.
Approach D: Synthetic Minority Oversampling (SMOTE / GANs)
Algorithmic generation of artificial failure samples to balance positive and negative class ratios.

## Slide 9
CRITICAL EVALUATION
Why We Didn't Choose Them & What Is Future Scope
Clear justification of design trade-offs: what was rejected vs. what is a valuable future upgrade
Rejected / Not Recommended
Synthetic Data (SMOTE/GANs): REJECTED
Fabricates physically impossible operating states (e.g., power at zero wind). Ruled out to preserve physical validity.
Unsupervised Clustering (K-Means/PCA): NOT WORTH IT
Produced intolerable false alarm rates on offshore weather outliers. Simple clustering lacks temporal context.
End-to-End Deep Learning for 10-Min SCADA: REJECTED
With 22 total events, deep neural nets severely overfit, require heavy compute, and destroy interpretability.
Valuable Future Scope
Physics-Informed Neural Networks (PINNs): FUTURE SCOPE
Embedding Navier-Stokes and heat diffusion differential equations directly into loss functions for thermodynamic modeling.
High-Frequency Vibration Telemetry: FUTURE SCOPE
Integrating 10-kHz accelerometer streams for bearing inner/outer race defect frequency analysis (BPFO/BPFI).
Cross-Farm Transfer Learning: FUTURE SCOPE
Domain-adaptation models transferring failure patterns learned from Farm A (Portugal) to offshore Farm C (Germany).

## Slide 10
THEORETICAL CHALLENGE 4
The Black-Box Trust Problem: SHAP & LIME
Why operators reject unexplained alerts and how XAI proved physical fidelity
The Operator's Dilemma
• If an AI flags a turbine as '90% Risk' without explanation, maintenance crews will ignore it.
• Technicians must know WHICH component to inspect: the gearbox, the generator, or the transformer?
• Black box predictions create distrust and alert fatigue.
How SHAP Solves It
• TreeSHAP calculates exact additive Shapley values based on game theory.
• Allocates exact risk 'points' to every individual sensor channel.
• Global SHAP reveals fleet-wide thermal drift drivers.
• Local SHAP waterfalls explain the exact alert moment for a specific turbine.
Ground Truth Match
• GEARBOX (Ev 72): Top SHAP feature was gearbox bearing temperature (+4.3°C rise).
• GENERATOR (Ev 0): Drive-end bearing temperature surged to 76°C-94°C, triggering alarm.
• TRANSFORMER (Ev 68): Phase L1 reached 117°C, dominating local SHAP attributions.
• HEALTHY (Ev 25): Negative scores across all components (zero alarm).

## Slide 11
THEORETICAL CHALLENGE 5
Asymmetric Financial Economics & Thresholding
Why standard 50% accuracy fails in operations, and how cost matrices save millions
The Asymmetric Cost Matrix
• MISSED FAILURE (False Negative): $150,000 - $300,000. Shattered gearbox, offshore vessel chartering, 6 weeks lost power.
• FALSE ALARM (False Positive): $3,500. Remote log diagnostics and routine technician inspection visit.
• PLANNED REPAIR (True Positive): $8,000. Uptower bearing replacement during scheduled calm weather window.
• CRITICAL REALITY: Missing a breakdown is 40 TIMES MORE EXPENSIVE than sending a technician on a false alarm!
The Cost-Optimal Threshold
• In textbooks, models use a 0.50 (50%) decision threshold.
• In wind energy, a 50% threshold allows too many catastrophic gearboxes to slip through.
• By plotting the Total Fleet Cost Curve, we discovered the economically optimal threshold is 0.30 - 0.35.
• This sweet spot catches impending failures 8 to 34 days early while keeping technician inspection costs under control.

## Slide 12
DECISION SUPPORT
Deployment: The Production Shiny Dashboard
Empowering wind farm operators and financial executives with interactive analytics
5 Operational Dashboard Tabs
1. Fleet Overview:
Live status cards across 3 wind farms, turbine catalog & event registry.
2. SCADA Telemetry Studio:
Multi-sensor time-series plots (Delta T, wind, power) + real-time risk timeline.
3. Model Benchmark & CARE:
Leave-One-Turbine-Out validation stats, confusion matrix & lead times.
4. Explainable AI Studio:
Interactive SHAP waterfall and LIME rules for every failure mode.
5. Business ROI Calculator:
Interactive cost sliders calculating net fleet dollar savings.
Deployment & Running Locally
BUILT WITH R & BSLIB: Modern industrial Darkly theme with responsive cards and SVG icons.
INSTANT LAUNCH: One-click launcher script in the project root:
Rscript run_app.R
Or inside an active R session / RStudio:
shiny::runApp('shiny_app')
Runs on http://127.0.0.1:3838 with instant reactive plots, requiring zero cloud dependencies.

## Slide 13
SUMMARY & KEY TAKEAWAYS
The 5-Point Presenter's Cheat Sheet
Everything you need to deliver a convincing, memorable presentation
1. Real Physics, Not Fake Data — Rejected synthetic SMOTE and purged post-trip status codes; 100% genuine sensor telemetry.
2. The 'Rising Fever' Method — Differential temperatures (Delta T) subtracted weather fluctuations and exposed true mechanical friction.
3. Sub-Second Speed — XGBoost trains in 0.67 seconds on 100k rows (109 MB RAM), reaching 0.83 AUC on completely unseen turbines.
4. 8 to 34 Days Lead Time — Achieved multi-week early warning across gearboxes, generator bearings, transformers, and hydraulics.
5. Explainable & Actionable — SHAP and LIME prove alerts match physical components; Shiny dashboard empowers operators with ROI calculators.